## ITEM1DS
|  | MZ Aspiratori S.P.A. | [7 empty] | Date |  |  |  | 11/02/2026 | [6 empty] | page |  |  | 1/4
[10 empty] | offer n° | [10 empty] | project
|  | VIA A.CERTANI 7 | [7 empty] | From |  |  |  | Steven Zweegers
|  | 40054 BUDRIO (BO) | [7 empty] | address |  |  |  | Algolweg 2, 3821 BH Amersfoort
|  | TEL +39 051 801981 | [7 empty] | reference | [10 empty] | Int. reference
|  | FAX +39 051 802974 | [7 empty] | telephone | [10 empty] | fax
[10 empty] | e-mail |  |  | steven@slingerlandtechniek.nl
Customer
http://www.mzaspiratori.eu | [9 empty] | address
info@mzaspiratori.com | [9 empty] | reference | [10 empty] | Int. reference
commerciale@mzaspiratori.com | [9 empty] | telephone | [10 empty] | fax
ordini@mzaspiratori.com | [9 empty] | e-mail
ITEM1 | [9 empty] | Document printed by Aeraulica - Dimensions and performances can be changed without prior notice
Type and characteristics of the requested machine | [15 empty] | performance on | [8 empty] | Inlet
Flow rate | [6 empty] | 5400 |  |  |  |  | [m3/h] |  |  |  | Capacity (Normal) | [8 empty] | 4710 |  |  |  | [Nm3/h]
Total pressure | [15 empty] | Static pressure | [8 empty] | 4500 |  |  |  | [Pa]
Working fluid temperature | [6 empty] | 40 |  |  |  |  | [°C] |  |  |  | Fluid specific weight | [8 empty] | 1,127 |  |  |  | [Kg/m3]
Installation altitude | [6 empty] | 0 asl |  |  |  |  | [m] |  |  |  | Specific weight std | [8 empty] | 1,204 |  |  |  | [Kg/m3]
Temperature |  |  |  |  | 40 |  |  |  | 20 |  |  |  |  | [°C] |  | Model Selected | [8 empty] | GR 560/2-I
Altitude |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | [m]
Humidity |  |  |  |  | 0 |  |  |  | 0 |  |  |  |  | [%] | [10 empty] | Execution |  |  | E04
Fluid specific weight |  |  |  |  | 1,127 |  |  |  | 1,204 |  |  |  |  | [Kg/m3] |  | Installation Type |  |  |  | D - Ducted inlet and ducted outlet
Total pressure |  |  |  |  | 4522 |  |  |  | 4831 |  |  |  |  | [Pa] |  | Revolution fan speed | [10 empty] | 2960 |  | [rpm]
Static pressure |  |  |  |  | 4400 |  |  |  | 4700 |  |  |  |  | [Pa] |  | Orientation | [10 empty] | LG 0
Flow rate |  |  |  |  | 5400 |  |  |  | 5400 |  |  |  |  | [m3/h] |  | Sound power LwA | [10 empty] | 98,47 |  | [db(A)]
Capacity (Normal) |  |  |  |  | 4710 |  |  |  | 5032 |  |  |  |  | [Nm3/h] |  | Sound pressure at mt.1,5 - 1/2 sf in open field | [10 empty] | 85,17 |  | [db(A)]
Power dem. at shaft |  |  |  |  | 9,28 |  |  |  | 9,913 |  |  |  |  | [kW] |  | Pipings |  |  | s>3mm = +3dB; 1mm<s<3mm = +4,5dB ; s<1mm = +6dB
Motor power demand |  |  |  |  | 9,28 |  |  |  | 9,913 |  |  |  |  | [kW] |  | Fan efficiency | [5 empty] | Inlet |  |  |  |  | 73,1 |  | %
Characteristics of chosen motor | [14 empty] | Motor efficiency IEC 60034-30 | [7 empty] | IE3 |  | PD2 impeller |  |  | 2,4 |  | kgm2
Code | 160MB2-50/std3 | [8 empty] | shape |  |  | B3 |  | Efficiency |  |  | 92 |  | 92 |  |  | 91 |  | PD2 needed |  |  | 2,4 |  | kgm2
Rated power |  |  |  | 15 |  | [kW] | n° poles |  |  | 2 | rpm |  | 2960 |  | Load |  |  | 100% |  | 75% |  |  | 50% |  | PD2 motor |  |  | 16,9 |  | kgm2
ErP 2009/125/CE Regulament (UE) N. 327/2011 | [11 empty] | Notes
Efficiency grade | [5 empty] | 64 |  | N | [6 empty] | 74,2 |  |  | Total efficiency | [8 empty] | 74,32 |  | %
Impeller type |  |  | backward blades |  |  |  |  | Type of test |  |  |  | B/total |  |  | Flow rate |  | 7821,72 |  |  | [m3/h] |  |  | Pressure |  |  | 3770 |  |  | [Pa]
NOTE
Rpm Limit |  | 3200 Rpm
values of the noise of fan obtained in ambient not reverberant with inlet and outlet ducts fully insulated

## ITEM1CE
| MZ Aspiratori S.P.A. |  |  | Date |  |  | 11/02/2026 |  |  |  |  | page |  |  | 2/4
|  |  |  | offer n° | [7 empty] | project
| VIA A.CERTANI 7 |  |  | From |  |  | Steven Zweegers
| 40054 BUDRIO (BO) |  |  | address |  |  | Algolweg 2, 3821 BH Amersfoort
| TEL +39 051 801981 |  |  | reference | [7 empty] | Int. reference
| FAX +39 051 802974 |  |  | telephone | [7 empty] | fax
|  |  |  | e-mail |  | steven@slingerlandtechniek.nl
Customer
http://www.mzaspiratori.eu |  |  |  | address
info@mzaspiratori.com |  |  |  | reference | [7 empty] | Int. reference
commerciale@mzaspiratori.com |  |  |  | telephone | [7 empty] | fax
ordini@mzaspiratori.com |  |  |  | e-mail
ITEM1 |  |  |  | Document printed by Aeraulica 2.0 - Dimensions and performances can be changed without prior notice
OFFER VALUE
Main items included in the offers | [15 empty] | Qty | Gross price each €
Fan | GR 560/2-I | [6 empty] | EXECUTION |  | E04 |  | [rpm] |  | 2960 |  | 1 | 1112
| Orientamento | LG 0 | 15 | [kW] | n° poles |  |  | 2 | 50 | [Hz] | B3 |  | G. | 160
Motor | Innomotics kW 15 2P 400/690V 50Hz IE3 | [14 empty] | 1 | 2134
Variation to standard construction, accessories
SA | Front support fixed at the inlet cone | [14 empty] | 1 | ---
MNE | Assembling and testing standard fan | [14 empty] | 1 | 71
FSTD | Standard fan painting RAL 5010 | [14 empty] | 1 | ---
Impeller 50 Hz
Class I - D: 0,56 [m]
40 [°C], 0 asl [m], 1,127 [Kg/m3]
[12 empty] | TOTALE |  |  |  | € | 498
[12 empty] | Discount |  |  |  | % | 0
[12 empty] | Sale price |  |  |  | € | 493.02
Signature

## ITEM1MS
|  | MZ Aspiratori S.P.A. | [5 empty] | Date |  |  | 11/02/2026 |  |  |  |  | page |  | 3/4
[8 empty] | offer n° | [7 empty] | project
|  | VIA A.CERTANI 7 | [5 empty] | From |  |  | Steven Zweegers
|  | 40054 BUDRIO (BO) | [5 empty] | address |  |  | Algolweg 2, 3821 BH Amersfoort
|  | TEL +39 051 801981 | [5 empty] | reference | [7 empty] | Int. reference
|  | FAX +39 051 802974 | [5 empty] | telephone | [7 empty] | fax
[8 empty] | e-mail |  | steven@slingerlandtechniek.nl
Customer
http://www.mzaspiratori.eu | [7 empty] | address
info@mzaspiratori.com | [7 empty] | reference | [7 empty] | Int. reference
commerciale@mzaspiratori.com | [7 empty] | telephone | [7 empty] | fax
ordini@mzaspiratori.com | [7 empty] | e-mail
ITEM1 | [7 empty] | Document printed by Aeraulica 2.0 - Dimensions and performances can be changed without prior notice
Indicative measures in the standard configuration. For detailed information contact your reference.
Indicative value of weight including standard motor.
B | I |  | H |  | H1 |  | H2 |  | J |  |  | K |  | M | Q |  | S | U | Φ | PD2
792 | 337 |  | 670 |  | 400 |  | 670 |  | 395 |  |  | 440 |  | 446 | 54 |  | 340 | 754 | 14 | 2,4
kg
240
Cod |  | dxn° |  | d1 |  | d2 |  | Φ |  | E1 |  |  | Cod |  | axb |  | a1 | b1 | a2 | b2
0360 A |  | 360x8 |  | 405 |  | 440 |  | 12 |  | 4 |  |  | 0361x0256 |  | 361x256 |  | 405 | 300 | 441 | 336
[13 empty] | N1xp |  | N2xp |  | n° | Φ | E
[13 empty] | 1x125 |  | 2x125 |  | 10 | 12 | 4

## CVGB
| date | 11/02/2026 | page | 4/4
| offer n° |  | order n° |  | progetto
GENERAL TERMS AND CONDITIONS OF SALE OF MZ ASPIRATORI S.p.A. GROUP